| WPG275*8 DIESEL GENERATING SET |  |
| --- | --- |

GENERATING SET RATINGS 50Hz – 1500rpm @ 0.8p.f. Voltage; PRP; ESP. V; kVA; kWe; kVA; kWe. 400/230; 250; 200; 275; 220.

| PRODUCT FEATURES |  |  |
| --- | --- | --- |
| Engine |  |  |
| •Cast iron frame style body structure •One-piece forged crankshaft |  |  |
| •Separate cast iron cylinder heads and replaceable dry cylinder liners •Aluminum alloy pistons with oil cooling gallery |  |  |
| Cooling system |  |  |
| •Radiator and hoses supplied separately •Thermostatically-controlled system with belt driven coolant pump and pusher fan |  |
| Fuel system |  |  |
| •P type fuel injection pump and injector for higher inject pressure • Duplex fine filter and water separation filter assembly with transparent cup for better efficiency |  |  |
| Lubrication system |  |  |
| •Flat bottom large capacity oil pan •Spin-on full-flow lube oil filter •High capacity gear driven lube oil pump |  |  |
| Electrical system |  |
| •24 Vdc electric starter motor and battery charging alternator • LOP + HWT sensors |  |
| Air intake and exhaust system |  |
| • Mid-position and below inlet turbocharger optimized or genset application • Special rear mounted air filter with restriction indicator • Exhaust manifold shield for heat isolating |  |
| Alternator |  |
| •Brushless, 4 Pole, IP23 drip-proof revolving field design •Class H insulation and Class H temperature rise |  |
| •Low reactance with 2/3 pitch windings on the stator |  |
| •Direct-coupled by flexible disc •Sustained overcurrent >300% in 10 sec |  |
| •Direct drive centrifugal blower fan cooling |  |
| Control module |  |
| •DSE control module is ideal for a wide control range to manage, monitor, and diagnose quickly and easily. •Display status message Provide protection Auto shutdown at fault detection |  |

| GENERATING SET SPECIFICATIONS |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Governor and regulation class |  |  | In accordance to ISO 8528-5 Class G2 performance |  |  |  |
| Phase number and connection |  |  | 3 phase, 4 wires, Y-type |  |  |  |
| Cooling method |  |  | Closed looped water-cooled |  |  |  |
| Starting method |  |  | DC 24V Electric starter |  |  |  |
| Steady-state voltage deviation |  |  | ≤± 2.5% |  |  |  |
| Steady-state frequency band |  |  | ≤1.5% |  |  |  |
| ENGINE |  |  |  |  |  |  |
| Brand / Model |  |  |  |  | Weichai / WP10D264E200 |  |
| Gross Power |  | kWm |  |  | ESP - 264 / PRP - 240 |  |
| Cylinder / Type / Aspiration |  |  |  |  | 6 / In-line / Turbocharged and Aftercooled |  |
| Bore x Stroke |  | mm |  |  | 126 x 130 |  |
| Displacement |  | L |  |  | 9.726 |  |
| Compression ratio |  |  |  |  | 17:1 |  |
| Brake Mean Effective Pressure |  | kPa |  |  | ESP – 2171 |  |
| COOLING SYSTEM |  |  |  |  |  |  |
| Type of Coolant |  |  |  |  | Liquid (water + 50% antifreeze) |  |
| Total Cooling System Capacity (with Radiator) |  |  |  | L | 35 |  |
| Max coolant temperature – shutdown |  |  |  | °C | 105 |  |
| Cooling Fan Airflow |  |  |  | m3/min | 415 |  |
| LUBRICATION SYSTEM |  |  |  |  |  |  |
| Operating Temperature range before Engine |  |  |  | °C |  | 78 -105 |
| Oil fuel consumption ratio based on engine fuel consumption data |  |  |  | g/kW.hr |  | ≤ 0.2% |
| Total system capacity (including filters) |  |  |  | L |  | 30 |
| Type of oil filter |  |  |  |  |  | Spin-on full flow filter |

| FUEL SYSTEM |  |  |  |  |
| --- | --- | --- | --- | --- |
| Type of fuel filter |  |  | Spin-on fuel filter |  |
| Min. internal diameter of the supply pipe |  | mm | 12 |  |
| Min. internal diameter of the return pipe |  | mm | 12 |  |
| Max. fuel return restriction |  | Bar | 0.5 |  |
| Max. fuel inlet temperature |  | °C | 50 |  |
| Fuel supply flow |  | L/hr | 169 |  |
| Fuel Consumption (Tolerance +3%) |  |  |  |  |
| Rating |  | gr/kWh |  | L/hr |
| 100%ESP |  | 201.6 |  | 63.4 |
| 100%PRP |  | 199.1 |  | 56.9 |
| 75% PRP |  | 197 |  | 42.2 |
| 50% PRP |  | 198.3 |  | 28.3 |
| 25% PRP |  | 215.5 |  | 15.4 |
| EXHAUST SYSTEM |  |  |  |  |
| Exhaust Gas temperature after the turbocharger |  | °C | 600 |  |
| Exhaust Gas flow |  | m3/min | ESP – 50.6 / PRP – 46.8 |  |
| Max. Exhaust back pressure |  | mBar | 60 |  |

| ALTERNATOR |  |  |
| --- | --- | --- |
| Brand / Model | WEICHAI / WHA-250-4/0.4 | LEROY-SOMER / TAL A46 D |
| Rated Current | 361A | 361A |
| Coupling / No. of Bearing | Direct / Single | Direct / Single |
| Winding Pitch | 2/3 | 2/3 |
| Type of Excitation | Self-excitation | Self-excitation |
| Cooling type | Air | Air |
| Voltage regulation method | AVR | AVR |
| Insurance | Class H | Class H |
| Temperature rise | Class H | Class H |
| Protection Grade | IP23 | IP23 |
| Efficiency at 0.8p.f.@100% load | 92.7% | 91.3% |

| CONTROL MODULE |  |  |  |
| --- | --- | --- | --- |
| Back-lit LCD display |  |  |
| 3 Phase generator and 3 Phase Mains monitoring |  |  |
| Monitoring speed, frequency, voltage, current, oil pressure, coolant temperature and fuel level |  |  |
| Display warning, shutdown and engine status information |  |  |
| Hours counter provides accurate information for monitoring and maintenance. |  |  |

STANDARD CONDITIONS

Standard operating environment: ambient temperature is 5℃~40℃,the altitude is less than 1000m,the relative humidity is less than 90%(25℃),and there is no dust, sand dust, salt fog, mold, condensation environment, etc. If the operating environment exceeds the above requirements, please contact the factory and consult.

| Ambient adaptability protection measures for alternators |  |  |
| --- | --- | --- |
| Ambient type | Ambient description | Measures of protection |
| General Ambient | The air is clean and dry, the humidity is ≤90%, and the distance from the coastline is ≥ 30km; Non-industrial ambient (chemical splash, acid-base steam, corrosive environment, etc.) | standard configuration |
| Humid Ambient | The humidity above 90% or condensation occurs | Anti-condensation heating |
| Salt spray Ambient | Salt fog crystals are produced in seaside (< 30km from the coastline) or island Ambient | Anti-condensation heating; Spray three-proof paint on winding surface; Spraying epoxy protection for parts and structures. |
| Dust Ambient | The ambient where mining, building construction, desert Gobi or sandstorm occur | Improve the protection level of the alternator to IP44; Install filters. |
| If you need to use protective measures beyond the standard, please contact the factory and consult. |  |  |

Special working condition

If the operating conditions of the generator meet the following conditions, please contact the factory and consult. - Multistage parallel operation - Grid-connected operation - As the main power supply, it runs continuously for a long time - The load includes a high power motor type load - Capacitive load - Special ambient such as high temperature, cold and plateau

| Ratings definitions Emergency Standby Power (ESP): Emergency Standby Power is the maximum power available for a varying load for the duration of a main power network failure. The average load factor over 24 hours of operation should not exceed 70% of the engine’s ESP power rating. Typical operational hours of the engine are 200 hours per year, with a maximum usage of 500 hours per year. This includes an annual maximum of 25 hours per year at the ESP power rating. No overload capability is allowed. The engine is not to be used for sustained utility paralleling applications. Prime power (PRP): Prime Power is the maximum power available for unlimited hours of usage in a variable load application. The average load factor should not exceed 70% of the engine’s PRP power rating during any 24 hour period. An overload capability of 10% is available; however, this is limited to 1 hour within every 12 hour period. |  |
| --- | --- |
|  | This outline drawing is to provide representative configuration details for Model series only. See respective model data sheet for specific model outline drawing number. Do not use for installation design |

Ddimension and Weight

| Structure | Model | Dim “A” mm | Dim “B” mm | Dim “C” mm | Dry wt.* kg | Fuel capacity* L |
| --- | --- | --- | --- | --- | --- | --- |
| Open | WPG275F8 | 2999 | 1170 | 1920 | 2440 | 411 |
| Silence（Elite） | WPG275L8 | 3900 | 1350 | 2050 | 3160 | 577 |
| Silence（Premium） | WPG275L8 | 4200 | 1350 | 2040 | 3360 | 324 |

* Note: Weights represent a set with standard features. See outline drawings for weights of other configurations.

Fuel capacity is the total capacity, including the fuel that cannot be pumped.

Codes and standards

| ISO 9001 | This generating set is designed and manufactured in facilities certified to ISO 9001. | ISO 8528 | This generating set has been designed to comply with ISO 8528 regulation. |
| --- | --- | --- | --- |
|  | The CE marking is only valid when equipment is used in a fixed installation application. Material compliance declaration is available upon request. |  |  |

For more information contact your local Weichai distributor or visit www.weichai.com